# Modbus_RTU Communication Description

Version: Version 1.0, November 2024

Modbus_RTU Communication DescriptionThe agreement number included in this agreementCommunication data formatFrame formatDevice register addressFault code tableWarning Code DescriptionPower flow sign descriptionCRC checksum algorithm

## The agreement number included in this agreement

- No. 3, No. 4, No. 5, No. 6

## Communication data format

- During communication, data is sent back in the form of words (WORD - 2 bytes). In each word sent back, the high byte is in front and the low byte is in the back. If two words are sent back continuously (such as long integer), the high word is in front and the low word is in the back.

| Data Type | Number of registers | Number of bytes | illustrate |
| --- | --- | --- | --- |
| Character | 1 | 1 | Send back two characters at a time, and fill them with 0 if they are less than two. |
| Integer | 1 | 2 | Send back once, high byte first, low byte last |
| Long integer | 2 | 4 | Send back in two words, with the high word first and the low word last |

## Frame format

### Register content query (function code 03H)

The query's starting and ending addresses must be the starting and ending addresses of a complete data block; otherwise, the returned data will be incorrect. For example, if the device serial number register's starting address is 186 and its length is 12, the query's starting address cannot be between 186 and 198, and the ending address (starting address + number of registers read) cannot fall within this range.

#### Frame format sent by the host computer

| Byte order | Code | Example | illustrate |
| --- | --- | --- | --- |
| 0 | Device Address | 01H | Device address (1~247) |
| 1 | 03H | 03H | Function code |
| 2 | Starting register address high byte | 00H | Register address high 8 bits |
| 3 | Starting register address low byte | 10H | Register address lower 8 bits |
| 4 | Register number high byte | 00H | High 8 bits of register number |
| 5 | Register number low byte | 02H | Low 8 bits of register number |
| 6 | CRC16 check high byte | C0H | CRC16 check high 8 bits |
| 7 | CRC16 check low byte | CBH | CRC16 check lower 8 bits |

#### The lower computer successfully parses and returns the frame format

| Byte order | Code | illustrate |
| --- | --- | --- |
| 0 | Device Address | Device address (1~247) |
| 1 | 03H | Function code |
| 2 | Number of bytes of data sent back (N) | N = Number of registers requested*2 |
| 3 | The first register data high byte |  |
| 4 | The first register data low byte |  |
| ...... | ...... |  |
| ...... | ...... |  |
|  | Nth register data high byte |  |
|  | Nth register data low byte |  |
| N+3 | CRC16 check high byte | All bytes before CRC must be checked |
| N+4 | CRC16 check low byte |  |

#### Lower computer parses error and returns frame format

| Byte order | Code | illustrate |
| --- | --- | --- |
| 0 | Device Address | Device address (1~247) |
| 1 | 03H | Function code |
| 2 | Number of bytes of data sent back (N) | N = Number of registers requested*2 |
| 3 | The first 0 | A total of N 0s are sent back |
| 4 | The second 0 |  |
| ...... | ...... |  |
| ...... | ...... |  |
|  | The N-1th 0 |  |
|  | Nth 0 |  |
| N+3 | CRC16 check high byte | All bytes before CRC must be checked |
| N+4 | CRC16 check low byte |  |

#### Register read example:

Read the total mains current RMS value (starting register 202) to the total mains active power data, where the total mains current returns 5.0A, the mains frequency returns 50.0Hz, and the total mains active power returns 1200w

Host computer: 01 03 00 CA 00 03 25 F5

Lower computer: 01 03 06 00 32 13 88 04 B0 9F 6B

### Register content setting (function code 10H)

#### Frame format sent by the host computer

| Byte order | Code | Example | illustrate |
| --- | --- | --- | --- |
| 0 | Device Address | 01H | Device address (1~247) |
| 1 | 10H | 10H | Function code |
| 2 | Starting register address high byte | 01H | Register address high 8 bits |
| 3 | Starting register address low byte | 10H | Register address lower 8 bits |
| 4 | Register number high byte | 00H | High 8 bits of the register number (always equal to 0) |
| 5 | Register number low byte | 02H | Low 8 bits of register number |
| 6 | Number of bytes to be written (N) |  | N = number of registers * 2 |
| 7 | The first register data high byte |  |  |
| 8 | The first register data low byte |  |  |
| ...... | ...... |  |  |
| ...... | ...... |  |  |
|  | Nth register data high byte |  |  |
|  | Nth register data low byte |  |  |
| N+7 | CRC16 check high byte |  | CRC16 check high 8 bits |
| N+8 | CRC16 check low byte |  | CRC16 check lower 8 bits |

#### The lower computer successfully parses and returns the frame format

| Byte order | Code | Example | illustrate |
| --- | --- | --- | --- |
| 0 | Device Address | 01H | Device address (1~247) |
| 1 | 10H | 10H | Function code |
| 2 | Starting register address high byte | 01H | Register address high 8 bits |
| 3 | Starting register address low byte | 10H | Register address lower 8 bits |
| 4 | Register number high byte | 00H | High 8 bits of the register number (always equal to 0) |
| 5 | Register number low byte | 02H | Low 8 bits of register number |
| 6 | CRC16 check high byte | 41H | CRC16 check high 8 bits |
| 7 | CRC16 check low byte | F1H | CRC16 check lower 8 bits |

#### Lower computer parses error and returns frame format

| Byte order | Code | illustrate |
| --- | --- | --- |
| 0 | Device Address | Device address (1~247) |
| 1 | 90H | Function code |
| 2 | Error Code | Error Code |
| 3 | CRC16 check high byte | CRC16 check high 8 bits |
| 4 | CRC16 check low byte | CRC16 check lower 8 bits |

#### Error code description

| Code | illustrate |
| --- | --- |
| 01H | A read-only register was operated |
| 03H | Writing data that exceeds the acceptable range |
| 07H | Registers that are not allowed to be modified in the current working mode |

#### Register write example:

Set the output voltage (starting register 606) to 220V

| Data Name | Unit | Data format | Starting address | Number of registers | Read and Write | illustrate | Valid protocol number |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Equipment fault code |  | ULong | 100 | 2 | R | 32-bit fault code, each bit corresponds to a fault code, see the fault code table for details , fault code 1 corresponds to bit 1, fault code 2 corresponds to bit 2, and so on | 3 ¦ 4 ¦ 5 ¦ 6 |
| Get the warning code for unshielded processing |  |  | 104 | 2 |  | For details on the 32-bit warning code, see the warning code description. | 3 ¦ 4 ¦ 5 ¦ 6 |
| Device Type |  | UInt | 171 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Protocol Number |  | UInt | 184 | 1 | R | 0x03 | 3 |
| Protocol Number |  | UInt | 184 | 1 | R | 0x04 | 4 |
| Protocol Number |  | UInt | 184 | 1 | R | 0x05 | 5 |
| Protocol Number |  | UInt | 184 | 1 | R | 0x06 | 6 |
| Device serial number |  | ASC | 186 | 12 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Power flow status |  | UInt | 198 | 1 | R | See the power flow flag description for details. | 3 ¦ 4 ¦ 5 ¦ 6 |
| Working Mode |  | UInt | 201 | 1 | R | 0: Power on mode 1: Standby mode 2: Mains mode 3: Off-grid mode 4: Bypass mode 5: Charging mode 6: Fault mode | 3 ¦ 4 ¦ 5 ¦ 6 |
| Total mains current effective value | 0.1A | Int | 202 | 1 | R |  |  |
| Mains frequency | 0.01Hz | Int | 203 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Total mains active power | 1w | Int | 204 | 1 | R |  |  |
| Total city TV power | 1VA | Int | 205 | 1 | R |  |  |
| Mains charging power | 1w | Int | 206 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Power Flow State Extension |  | UInt | 207 | 1 | R | See the power flow flag description for details. | 3 ¦ 4 ¦ 5 ¦ 6 |
| Reserve |  |  | 208 | 18 |  |  |  |
| Total inverter current effective value | 0.1A | Int | 226 | 1 | R |  |  |
| Inverter frequency | 0.01Hz | Int | 227 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Total inverter active power | 1w | Int | 228 | 1 | R |  |  |
| Total inverter apparent power | 1VA | Int | 229 | 1 | R |  |  |
| Inverter charging current | 0.1A | Int | 230 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Inversion temperature | 1℃ | Int | 231 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Reserve |  |  | 232 | 20 |  |  |  |
| Total output current effective value | 0.1A | Int | 252 | 1 | R |  | 4 ¦ 6 |
| Output frequency | 0.01Hz | Int | 253 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Total output active power | 1w | Int | 254 | 1 | R |  | 4 ¦ 6 |
| Total output apparent power | 1w | Int | 255 | 1 | R |  | 4 ¦ 6 |
| Total load percentage | 1% | Int | 256 | 1 | R |  | 4 ¦ 6 |
| Reserve |  |  | 257 | 20 |  |  |  |
| Average battery voltage | 0.1v | Int | 277 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Battery current filtered average value | 0.1A | Int | 278 | 1 | R | Positive numbers indicate charging, negative numbers indicate discharging | 3 ¦ 4 ¦ 5 ¦ 6 |
| Average battery power | 1w | Int | 279 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Battery percentage | 1% | UInt | 280 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| DCDC temperature | 1℃ | Int | 281 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Reserve |  |  | 282 | 20 |  |  |  |
| Average total PV power | 1w | Int | 302 | 1 | R |  | 3 ¦ 4 |
| Average total PV charging power | 1w | Int | 303 | 1 | R |  | 3 ¦ 4 |
| Average total PV charging current | 0.1A | Int | 304 | 1 | R |  | 3 ¦ 4 |
| PV temperature | 1℃ | Int | 305 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Reserve |  |  | 306 | 20 |  |  |  |
| Total external CT sampling power | 1w | Long | 326 | 2 | R | Positive number: the grid outputs energy; negative number: energy is injected into the grid |  |
| Reserve |  |  | 328 | 10 |  |  |  |
| Mains L1 voltage effective value | 0.1v | Int | 338 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Mains L1 current effective value | 0.1A | Int | 339 | 1 | R |  |  |
| Mains L1 active power | 1w | Int | 340 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Apparent power of mains L1 | 1VA | Int | 341 | 1 | R |  |  |
| Inverter L1 voltage effective value | 0.1v | Int | 342 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Inverter L1 current effective value | 0.1A | Int | 343 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Inverter L1 active power | 1w | Int | 344 | 1 | R | Positive numbers indicate inverter output, negative numbers indicate inverter input | 3 ¦ 4 ¦ 5 ¦ 6 |
| Inverter L1 apparent power | 1VA | Int | 345 | 1 | R |  |  |
| Output L1 voltage effective value | 0.1v | Int | 346 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Output L1 current effective value | 0.1A | Int | 347 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Output L1 active power | 1w | Int | 348 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Output L1 apparent power | 1VA | Int | 349 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Output L1 load percentage | 1% | Int | 350 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| PV1 voltage average value | 0.1v | Int | 351 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| PV1 current average value | 0.1A | Int | 352 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| PV1 power average value | 1w | Int | 353 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| L1 external CT sampling power | 1w | Long | 354 | 2 | R | Positive number: the grid outputs energy; negative number: energy is injected into the grid |  |
| Reserve |  |  | 356 | 20 |  |  |  |
| Mains L2 voltage effective value | 0.1v | Int | 376 | 1 | R |  |  |
| Mains L2 current effective value | 0.1A | Int | 377 | 1 | R |  |  |
| Average power of mains L2 | 1w | Int | 378 | 1 | R |  |  |
| Mains L2 apparent power | 1VA | Int | 379 | 1 | R |  |  |
| Inverter L2 voltage effective value | 0.1v | Int | 380 | 1 | R |  |  |
| Inverter L2 current effective value | 0.1A | Int | 381 | 1 | R |  |  |
| Average inverter L2 power | 1w | Int | 382 | 1 | R | Positive numbers indicate inverter output, negative numbers indicate inverter input |  |
| Inverter L2 apparent power | 1VA | Int | 383 | 1 | R |  |  |
| Output L2 voltage effective value | 0.1v | Int | 384 | 1 | R |  | 4 ¦ 6 |
| Output L2 current effective value | 0.1A | Int | 385 | 1 | R |  | 4 ¦ 6 |
| Output L2 power average | 1w | Int | 386 | 1 | R |  | 4 ¦ 6 |
| Output L2 apparent power | 1w | Int | 387 | 1 | R |  | 4 ¦ 6 |
| Output L2 load percentage | 1% | Int | 388 | 1 | R |  | 4 ¦ 6 |
| PV2 voltage average value | 0.1v | Int | 389 | 1 | R |  | 3 ¦ 4 |
| PV2 current average value | 0.1A | Int | 390 | 1 | R |  | 3 ¦ 4 |
| PV2 power average value | 1w | Int | 391 | 1 | R |  | 3 ¦ 4 |
| L2 external CT sampling power | 1w | Long | 392 | 2 | R | Positive number: the grid outputs energy; negative number: energy is injected into the grid |  |
| Reserve |  |  | 394 | 20 |  |  |  |
| Mains L3 voltage effective value | 0.1v | Int | 414 | 1 | R |  |  |
| Mains L3 current effective value | 0.1A | Int | 415 | 1 | R |  |  |
| Average power of mains L3 | 1w | Int | 416 | 1 | R |  |  |
| Mains L3 apparent power | 1VA | Int | 417 | 1 | R |  |  |
| Inverter L3 voltage effective value | 0.1v | Int | 418 | 1 | R |  |  |
| Inverter L3 current effective value | 0.1A | Int | 419 | 1 | R |  |  |
| Average inverter L3 power | 1w | Int | 420 | 1 | R | Positive numbers indicate inverter output, negative numbers indicate inverter input |  |
| Inverter L3 apparent power | 1VA | Int | 421 | 1 | R |  |  |
| Output L3 voltage effective value | 0.1v | Int | 422 | 1 | R |  |  |
| Output L3 current effective value | 0.1A | Int | 423 | 1 | R |  |  |
| Output L3 power average | 1w | Int | 424 | 1 | R |  |  |
| Output L3 apparent power | 1w | Int | 425 | 1 | R |  |  |
| Output L3 load percentage | 1% | Int | 426 | 1 | R |  |  |
| PV3 voltage average value | 0.1v | Int | 427 | 1 | R |  |  |
| PV3 current average value | 0.1A | Int | 428 | 1 | R |  |  |
| PV3 power average value | 1w | Int | 429 | 1 | R |  |  |
| L3 external CT sampling power | 1w | Long | 430 | 2 | R | Positive number: the grid outputs energy; negative number: energy is injected into the grid |  |
| Reserve |  |  | 432 | 168 |  |  |  |
| Output Mode |  | Uint | 600 | 1 | R/W | 0: Single machine; 1: Parallel machine; 2: Three-phase combination-P1 3: Three-phase combination-P2 4: Three-phase combination-P3 5: Split-phase-P1 6: Split-phase-P2 | 3 ¦ 4 ¦ 5 ¦ 6 |
| (Primary) Output Priority |  | Uint | 601 | 1 | R/W | 1: PV-mains-battery (SUB) [inversion priority] 2: PV-battery-mains (SBU) 3: PV-mains-battery (SUF) [PV can be connected to the grid] | 3 ¦ 4 ¦ 5 ¦ 6 |
| (Secondary) Output Priority |  | Uint | 602 | 1 | R/W | 0: Disable auxiliary output priority 1: PV-mains-battery (SUB) [priority for inversion] 2: PV-battery-mains (SBU) 3: PV-mains-battery (SUF) [PV can be connected to the grid] | 3 ¦ 4 ¦ 5 ¦ 6 |
| Auxiliary output priority start time |  | Uint | 603 | 1 | R/W | Range: 0000~2359, thousands and hundreds are hours, tens and units are minutes | 3 ¦ 4 ¦ 5 ¦ 6 |
| Secondary output priority end time |  | Uint | 604 | 1 | R/W | Range: 0000~2359, thousands and hundreds are hours, tens and units are minutes | 3 ¦ 4 ¦ 5 ¦ 6 |
| Output priority for the current period |  | Uint | 605 | 1 | R | 1: PV-mains-battery (SUB) [inversion priority] 2: PV-battery-mains (SBU) 3: PV-mains-battery (SUF) [PV can be connected to the grid] | 3 ¦ 4 ¦ 5 ¦ 6 |
| Output voltage setting value | 0.1v | Uint | 606 | 1 | R/W | 2200: 220v output; 2300: 230v output; 2400: 240v output; | 3 ¦ 4 ¦ 5 ¦ 6 |
| Output frequency setting value | 0.01Hz | Uint | 607 | 1 | R/W | 5000: 50Hz output; 6000: 60Hz output; | 3 ¦ 4 ¦ 5 ¦ 6 |
| OP2 overload alarm setting | 1% | Uint | 608 | 1 | R/W | Range: 10% ~ 100% | 4 ¦ 6 |
| Is OP2 allowed to output? |  | Uint | 609 | 1 | R/W | 0: Prohibit 1: Allow | 4 ¦ 6 |
| OP2 output start time |  | Uint | 610 | 1 | R/W | Range: 0~23. Set the start time to 0 and the end time to 23, which means that OP2 can be output all day long if the conditions are met. | 4 ¦ 6 |
| OP2 output end time |  | Uint | 611 | 1 | R/W | Range: 0~23. Set the start time to 0 and the end time to 23, which means that OP2 can be output all day long if the conditions are met. | 4 ¦ 6 |
| Reserve |  |  | 612 | 18 |  |  |  |
| Battery Type |  | Uint | 630 | 1 | R/W | 0: AGM; 1: FLD; 2: USER; 4: Li2 6: Li4 8: LiB | 3 ¦ 4 ¦ 5 ¦ 6 |
| Battery overvoltage protection point | 0.1v | Uint | 631 | 1 | R/W |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Battery charging priority |  | Uint | 632 | 1 | R/W | 1: PV first (SOF) 2: PV and mains at the same level (SNU) 3: Only PV charging allowed (OSO) 4: PV first to meet the output remaining charge (SOR) | 3 ¦ 4 ¦ 5 ¦ 6 |
| Secondary charging priority |  | Uint | 633 | 1 | R/W | 0: Disable auxiliary charging priority 1: PV priority (SOF) 2: PV and mains at the same level (SNU) 3: Only PV charging is allowed (OSO) 4: PV priority satisfies the output remaining charge (SOR) | 3 ¦ 4 ¦ 5 ¦ 6 |
| Auxiliary charging priority start time |  | Uint | 634 | 1 | R/W | Range: 0000~2359, thousands and hundreds are hours, tens and units are minutes | 3 ¦ 4 ¦ 5 ¦ 6 |
| Secondary charging priority end time |  | Uint | 635 | 1 | R/W | Range: 0000~2359, thousands and hundreds are hours, tens and units are minutes | 3 ¦ 4 ¦ 5 ¦ 6 |
| Charging priority for the current period |  | Uint | 636 | 1 | R | 1: PV first (SOF) 2: PV and mains at the same level (SNU) 3: Only PV charging allowed (OSO) 4: PV first to meet the output remaining charge (SOR) | 3 ¦ 4 ¦ 5 ¦ 6 |
| Maximum charging voltage | 0.1v | Uint | 637 | 1 | R/W |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Float charge voltage | 0.1v | Uint | 638 | 1 | R/W |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Waiting time for constant voltage to float charge | min | Uint | 639 | 1 | R/W | Range: 1~900min. If set to 0, the default is 10min. | 3 ¦ 4 ¦ 5 ¦ 6 |
| Maximum charging current | 0.1A | Uint | 640 | 1 | R/W |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Maximum AC charging current | 0.1A | Uint | 641 | 1 | R/W |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Maximum discharge current protection | 1A | Uint | 642 | 1 | R/W | Range: 0 ~ 500A | 3 ¦ 4 ¦ 5 ¦ 6 |
| Battery discharge recovery point in AC mode | 0.1v | Uint | 643 | 1 | R/W | Set to 0 to indicate full recovery | 3 ¦ 4 ¦ 5 ¦ 6 |
| Battery discharge protection point in AC mode | 0.1v | Uint | 644 | 1 | R/W |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Off-grid mode OP1 battery low voltage protection point | 0.1v | Uint | 645 | 1 | R/W |  | 4 ¦ 6 |
| Off-grid mode battery discharge protection point | 0.1v | Uint | 646 | 1 | R/W |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Battery discharge SOC protection value in AC mode | 1% | Uint | 647 | 1 | R/W |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Battery discharge SOC recovery value in AC mode | 1% | Uint | 648 | 1 | R/W |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Off-grid mode OP1 battery discharge SOC protection value | 1% | Uint | 649 | 1 | R/W |  | 4 ¦ 6 |
| Off-grid mode battery discharge SOC protection value | 1% | Uint | 650 | 1 | R/W |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Battery Eq mode enabled |  | Uint | 651 | 1 | R/W | 0: Disable; 1: Enable | 3 ¦ 4 ¦ 5 ¦ 6 |
| Eq charging voltage | 0.1v | Uint | 652 | 1 | R/W |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| bat_eq_time | min | Uint | 653 | 1 | R/W | Range: 0 ~ 900 | 3 ¦ 4 ¦ 5 ¦ 6 |
| Eq timeout exit | min | Uint | 654 | 1 | R/W | Range: 0 ~ 900 | 3 ¦ 4 ¦ 5 ¦ 6 |
| The interval between two Eq charging | day | Uint | 655 | 1 | R/W | Range: 1 ~ 90 | 3 ¦ 4 ¦ 5 ¦ 6 |
| Force Eq Charge |  | Uint | 656 | 1 | W | 1: Manually force Eq to charge once | 3 ¦ 4 ¦ 5 ¦ 6 |
| Reserve |  |  | 657 | 20 |  |  |  |
| Input Mode |  | Uint | 677 | 1 | R/W | 0: APL; 1: UPS; 2: GNT | 3 ¦ 4 ¦ 5 ¦ 6 |
| Buzzer mode |  | Uint | 678 | 1 | R/W | 0: Mute in all situations; 1: Sound when the input source changes or when there is a specific warning or fault; 2: Sound when there is a specific warning or fault; 3: Sound when there is a fault | 3 ¦ 4 ¦ 5 ¦ 6 |
| LCD backlight |  | Uint | 679 | 1 | R/W | 0: Timed off; 1: Constant on | 3 ¦ 4 ¦ 5 ¦ 6 |
| LCD automatically returns to the home page |  | Uint | 680 | 1 | R/W | 0: No automatic return; 1: Automatic return after 1 minute | 3 ¦ 4 ¦ 5 ¦ 6 |
| Energy saving mode switch |  | Uint | 681 | 1 | R/W | 0: Energy saving mode off; 1: Energy saving mode on | 3 ¦ 4 ¦ 5 ¦ 6 |
| Overload automatic restart |  | Uint | 682 | 1 | R/W | 0: No restart in case of overload fault; 1: Automatic restart in case of overload fault | 3 ¦ 4 ¦ 5 ¦ 6 |
| Over temperature automatic restart |  | Uint | 683 | 1 | R/W | 0: No restart on over-temperature fault; 1: Automatic restart on over-temperature fault | 3 ¦ 4 ¦ 5 ¦ 6 |
| Overload bypass enable |  | Uint | 684 | 1 | R/W | 0: Disable; 1: Enable | 3 ¦ 4 ¦ 5 ¦ 6 |
| Parallel PV detection mode |  | Uint | 685 | 1 | R/W | 0: ; 1: |  |
| External CT enable |  | Uint | 686 | 1 | R/W | 0: Disable; 1: Enable |  |
| Warning Mask [I] |  | ULong | 687 | 2 | R/W | Warnings corresponding to 1 are displayed normally, and warnings corresponding to 0 are blocked. | 3 ¦ 4 ¦ 5 ¦ 6 |
| Dry Contact |  | Uint | 689 | 1 | R/W | 0: Normal mode; 1: Grounded box mode; | 3 ¦ 4 ¦ 5 ¦ 6 |
| Automatic mains output enable |  | Uint | 690 | 1 | R/W | 0: No AC power output if the power button is not pressed 1: The AC power will automatically output if the power button is not pressed | 3 ¦ 4 ¦ 5 ¦ 6 |
| PV grid-connected maximum power | 1w | Uint | 691 | 1 | R/W | Range: 200w ~ rated power |  |
| Island detection enabled |  | Uint | 692 | 1 | R/W | 0: Disable 1: Enable |  |
| Boot method |  | Uint | 693 | 1 | R/W | 0: Can be powered on locally or remotely; 1: Can only be powered on locally; 2: Can only be powered on remotely | 3 ¦ 4 ¦ 5 ¦ 6 |
| Remote switch |  | Uint | 694 | 1 | R/W | 0: Remote shutdown 1: Remote startup | 3 ¦ 4 ¦ 5 ¦ 6 |
| Exit fault lock state |  | Uint | 695 | 1 | W | 1: Exit the fault lock state (only takes effect when the machine enters the fault mode) | 3 ¦ 4 ¦ 5 ¦ 6 |
| Inverter Date |  | Uint | 696 | 3 | R/W | Three 16-digit numbers representing the year, month, and day (e.g., 07H E6H 00H 07H 00H 0EH represents July 14, 2022) | 3 ¦ 4 ¦ 5 ¦ 6 |
| Inverter time |  | Uint | 699 | 3 | R/W | Three 16-digit numbers representing hours, minutes, and seconds (e.g., 00H 0DH 00H 0FH 00H 10H represents 13:15:16) | 3 ¦ 4 ¦ 5 ¦ 6 |
| Power generation on that day | 0.01kwh | Uint | 702 | 1 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Total power generation | 0.01kwh | ULong | 703 | 2 | R |  | 3 ¦ 4 ¦ 5 ¦ 6 |
| Zero power generation |  | Uint | 705 | 1 | W | 0xAA: Clear all power generation data | 3 ¦ 4 ¦ 5 ¦ 6 |
| Reset User Parameters |  |  | 706 | 1 | W | 0xAA: User parameters are restored to default values ​​(valid when working in non-off-grid mode) | 3 ¦ 4 ¦ 5 ¦ 6 |
| Ground relay enable |  |  | 707 | 1 | R/W | 0: Disable 1: Enable | 4 ¦ 6 |
| Lithium battery activation time | min |  | 709 | 1 | R/W | Range: 6 ~ 300 | 3 ¦ 4 ¦ 5 ¦ 6 |
| Lithium battery automatic activation enable |  | Uint | 858 | 1 | R/W | 0: Manual activation; 1: Automatic activation once after power on | 3 ¦ 4 ¦ 5 ¦ 6 |
| Lithium battery activation once |  | Uint | 859 | 1 | R/W | 0: Invalid 1: Run once lithium battery activation | 3 ¦ 4 ¦ 5 ¦ 6 |

Host computer: 01 10 02 5E 00 01 02 08 98 8E 84

Lower computer: 01 10 02 5E 00 01 61 A3

## Device register address

- R: Indicates readable, which means it supports 03H command. W: Indicates writable, which means it supports 10H command.

- Int: integer; Long: long integer; UInt: unsigned integer; ULong: unsigned long integer; ASC: ASCII code

- Max: take the maximum value; Min: take the minimum value

- At the same address, different protocol numbers have different data. Please refer to the column of valid protocol number. For example, at address 184, the device with protocol number 3 will return 3, and the device with protocol number 4 will return 4. The valid protocol number is empty and is considered invalid data.

- The addresses in the following table are expressed in decimal.

## Fault code table

| Fault Code | illustrate |
| --- | --- |
| bit0 | Inverter overtemperature |
| bit1 | PV overtemperature |
| bit2 | DCDC over temperature |
| bit3 | Battery overvoltage |
| bit4 | Reserve |
| bit5 | Output short circuit |
| bit6 | Inverter overvoltage |
| bit7 | Output overload |
| bit8 | Busbar overvoltage |
| bit9 | Bus soft start timeout |
| bit10 | PV overcurrent |
| bit11 | PV overvoltage |
| bit12 | DCDC overcurrent |
| bit13 | Inverter overcurrent |
| bit14 | Busbar low voltage |
| bit15 | reserve |
| bit16 | The inverter DC component is too high |
| bit17 | PV2 current zero deviation is too large |
| bit18 | Output current zero bias is too large |
| bit19 | Inverter current zero bias is too large |
| bit20 | Battery current zero bias is too large |
| bit21 | PV1 current zero deviation is too large |
| bit22 | Inverter low voltage |
| bit23 | Inverter negative power protection |
| bit24 | The host of the parallel system is lost |
| bit25 | The parallel system synchronization signal is abnormal |
| bit26 | Incompatible battery type |
| bit27 | Incompatible parallel versions |
| bit28 | External CT setup repeat |
| bit29 | Output 2 current zero deviation is too large |

## Warning Code Description

System warning is a 32-bit unsigned long integer. Each bit corresponds to a warning. Each bit can also be masked by the warning mask I. After masking, the corresponding warning will not be read on the LCD or through commands.

### Warning code table

| Warning Code | illustrate |
| --- | --- |
| bit 0 | Mains zero-crossing loss |
| bit 1 | Abnormal AC power waveform |
| bit 2 | Mains overvoltage |
| bit 3 | Mains undervoltage |
| bit 4 | Mains overfrequency |
| bit 5 | Mains underfrequency |
| bit 6 | PV1 undervoltage |
| bit 7 | Overheating |
| bit 8 | Low battery voltage |
| bit 9 | Battery not connected |
| bit 10 | Output overload |
| bit 11 | Battery Eq Charging |
| bit 12 | The battery is discharged to low voltage and has not yet been charged back to the recovery point |
| bit 13 | Output power derating |
| bit 14 | Fan stall |
| bit 15 | PV energy is too low to be used |
| bit 16 | Parallel communication interrupted |
| bit 17 | Single and parallel output modes are inconsistent |
| bit 18 | The voltage difference of the parallel batteries is too large |
| bit19 | Lithium battery communication abnormality |
| bit20 | The battery discharge current exceeds the set value |
| bit 21 | Island Detection |
| bit 22 | PV2 undervoltage |
| bit23 | Main output overload |
| bit24 | Sec output load exceeds the set value |
| bit25 | Sec output overload |
| bits 26 to 31 | reserve |

## Power flow sign description

The power flow is represented by a 16-bit unsigned integer. The meaning of each bit is as follows:

### Power flow table (corresponding to register 198)

| Bit | illustrate |
| --- | --- |
| bit0~1 | 0: PV is not connected to the system 1: PV is connected to the system |
| bit2~3 | 0: Mains power is not connected to the system 1: Mains power is connected to the system |
| bit4~5 | 0: Battery neither charged nor discharged 1: Battery charging 2: Battery discharging |
| bit6~7 | 0: The system does not output load 1: The system outputs load |
| bit8 | 0: Not charging with AC power 1: Charging with AC power |
| bit9 | 0: PV not charging 1: PV charging |
| bit10 | 0: Battery icon on 1: Battery icon off |
| bit11 | 0: PV icon is on 1: PV icon is off |
| bit12 | 0: Mains icon is on 1: Mains icon is off |
| bit13 | 0: Load icon is on 1: Load icon is off |

### Power flow table expansion (corresponding to register 207)

| Bit | illustrate |
| --- | --- |
| bit0 | 0: PV1 is not connected to the system 1: PV1 is connected to the system |
| bit1 | 0: PV2 is not connected to the system 1: PV2 is connected to the system |
| bit2~3 | 0: AC input 1 is not connected to the system 1: AC input 1 is connected to the system |
| bit4~5 | 0: AC input 2 is not connected to the system 1: AC input 2 is connected to the system |
| bit6-7 | 0: AC input 3 is not connected to the system 1: AC input 3 is connected to the system |
| bit8 | 0: Main output with load 1: Main output without load |
| bit9 | 0: Sec output with load 1: Sec no output |
| bit10-15 | Reserve |

## CRC checksum algorithm

Parameter model : CRC - 16 / MODBUS  X16 + X15 + X2 + 1

C language code

const  char  auchCRCHi [] = {

0x00 , 0xC1 , 0x81 , 0x40 , 0x01 , 0xC0 , 0x80 , 0x41 , 0x01 , 0xC0 ,

0x80 , 0x41 , 0x00 , 0xC1 , 0x81 , 0x40 , 0x01 , 0xC0 , 0x80 , 0x41 ,

0x00 , 0xC1 , 0x81 , 0x40 , 0x00 , 0xC1 , 0x81 , 0x40 , 0x01 , 0xC0 ,

0x80 , 0x41 , 0x01 , 0xC0 , 0x80 , 0x41 , 0x00 , 0xC1 , 0x81 , 0x40 ,

0x00 , 0xC1 , 0x81 , 0x40 , 0x01 , 0xC0 , 0x80 , 0x41 , 0x00 , 0xC1 ,

0x81 , 0x40 , 0x01 , 0xC0 , 0x80 , 0x41 , 0x01 , 0xC0 , 0x80 , 0x41 ,

0x00 , 0xC1 , 0x81 , 0x40 , 0x01 , 0xC0 , 0x80 , 0x41 , 0x00 , 0xC1 ,

0x81 , 0x40 , 0x00 , 0xC1 , 0x81 , 0x40 , 0x01 , 0xC0 , 0x80 , 0x41 ,

0x00 , 0xC1 , 0x81 , 0x40 , 0x01 , 0xC0 , 0x80 , 0x41 , 0x01 , 0xC0 ,

0x80 , 0x41 , 0x00 , 0xC1 , 0x81 , 0x40 , 0x00 , 0xC1 , 0x81 , 0x40 ,

0x01 , 0xC0 , 0x80 , 0x41 , 0x01 , 0xC0 , 0x80 , 0x41 , 0x00 , 0xC1 ,

0x81 , 0x40 , 0x01 , 0xC0 , 0x80 , 0x41 , 0x00 , 0xC1 , 0x81 , 0x40 ,

0x00 , 0xC1 , 0x81 , 0x40 , 0x01 , 0xC0 , 0x80 , 0x41 , 0x01 , 0xC0 ,

0x80 , 0x41 , 0x00 , 0xC1 , 0x81 , 0x40 , 0x00 , 0xC1 , 0x81 , 0x40 ,

0x01 , 0xC0 , 0x80 , 0x41 , 0x00 , 0xC1 , 0x81 , 0x40 , 0x01 , 0xC0 ,

0x80 , 0x41 , 0x01 , 0xC0 , 0x80 , 0x41 , 0x00 , 0xC1 , 0x81 , 0x40 ,

0x00 , 0xC1 , 0x81 , 0x40 , 0x01 , 0xC0 , 0x80 , 0x41 , 0x01 , 0xC0 ,

0x80 , 0x41 , 0x00 , 0xC1 , 0x81 , 0x40 , 0x01 , 0xC0 , 0x80 , 0x41 ,

0x00 , 0xC1 , 0x81 , 0x40 , 0x00 , 0xC1 , 0x81 , 0x40 , 0x01 , 0xC0 ,

0x80 , 0x41 , 0x00 , 0xC1 , 0x81 , 0x40 , 0x01 , 0xC0 , 0x80 , 0x41 ,

0x01 , 0xC0 , 0x80 , 0x41 , 0x00 , 0xC1 , 0x81 , 0x40 , 0x01 , 0xC0 ,

0x80 , 0x41 , 0x00 , 0xC1 , 0x81 , 0x40 , 0x00 , 0xC1 , 0x81 , 0x40 ,

0x01 , 0xC0 , 0x80 , 0x41 , 0x01 , 0xC0 , 0x80 , 0x41 , 0x00 , 0xC1 ,

0x81 , 0x40 , 0x00 , 0xC1 , 0x81 , 0x40 , 0x01 , 0xC0 , 0x80 , 0x41 ,

0x00 , 0xC1 , 0x81 , 0x40 , 0x01 , 0xC0 , 0x80 , 0x41 , 0x01 , 0xC0 ,

0x80 , 0x41 , 0x00 , 0xC1 , 0x81 , 0x40

} ;

const  char  auchCRCLo [] = {

0x00 , 0xC0 , 0xC1 , 0x01 , 0xC3 , 0x03 , 0x02 , 0xC2 , 0xC6 , 0x06 ,

0x07 , 0xC7 , 0x05 , 0xC5 , 0xC4 , 0x04 , 0xCC , 0x0C , 0x0D , 0xCD ,

0x0F , 0xCF , 0xCE , 0x0E , 0x0A , 0xCA , 0xCB , 0x0B , 0xC9 , 0x09 ,

0x08 , 0xC8 , 0xD8 , 0x18 , 0x19 , 0xD9 , 0x1B , 0xDB , 0xDA , 0x1A ,

0x1E , 0xDE , 0xDF , 0x1F , 0xDD , 0x1D , 0x1C , 0xDC , 0x14 , 0xD4 ,

0xD5 , 0x15 , 0xD7 , 0x17 , 0x16 , 0xD6 , 0xD2 , 0x12 , 0x13 , 0xD3 ,

0x11 , 0xD1 , 0xD0 , 0x10 , 0xF0 , 0x30 , 0x31 , 0xF1 , 0x33 , 0xF3 ,

0xF2 , 0x32 , 0x36 , 0xF6 , 0xF7 , 0x37 , 0xF5 , 0x35 , 0x34 , 0xF4 ,

0x3C , 0xFC , 0xFD , 0x3D , 0xFF , 0x3F , 0x3E , 0xFE , 0xFA , 0x3A ,

0x3B , 0xFB , 0x39 , 0xF9 , 0xF8 , 0x38 , 0x28 , 0xE8 , 0xE9 , 0x29 ,

0xEB , 0x2B , 0x2A , 0xEA , 0xEE , 0x2E , 0x2F , 0xEF , 0x2D , 0xED ,

0xEC , 0x2C , 0xE4 , 0x24 , 0x25 , 0xE5 , 0x27 , 0xE7 , 0xE6 , 0x26 ,

0x22 , 0xE2 , 0xE3 , 0x23 , 0xE1 , 0x21 , 0x20 , 0xE0 , 0xA0 , 0x60 ,

0x61 , 0xA1 , 0x63 , 0xA3 , 0xA2 , 0x62 , 0x66 , 0xA6 , 0xA7 , 0x67 ,

0xA5 , 0x65 , 0x64 , 0xA4 , 0x6C , 0xAC , 0xAD , 0x6D , 0xAF , 0x6F ,

0x6E , 0xAE , 0xAA , 0x6A , 0x6B , 0xAB , 0x69 , 0xA9 , 0xA8 , 0x68 ,

0x78 , 0xB8 , 0xB9 , 0x79 , 0xBB , 0x7B , 0x7A , 0xBA , 0xBE , 0x7E ,

0x7F , 0xBF , 0x7D , 0xBD , 0xBC , 0x7C , 0xB4 , 0x74 , 0x75 , 0xB5 ,

0x77 , 0xB7 , 0xB6 , 0x76 , 0x72 , 0xB2 , 0xB3 , 0x73 , 0xB1 , 0x71 ,

0x70 , 0xB0 , 0x50 , 0x90 , 0x91 , 0x51 , 0x93 , 0x53 , 0x52 , 0x92 ,

0x96 , 0x56 , 0x57 , 0x97 , 0x55 , 0x95 , 0x94 , 0x54 , 0x9C , 0x5C ,

0x5D , 0x9D , 0x5F , 0x9F , 0x9E , 0x5E , 0x5A , 0x9A , 0x9B , 0x5B ,

0x99 , 0x59 , 0x58 , 0x98 , 0x88 , 0x48 , 0x49 , 0x89 , 0x4B , 0x8B ,

0x8A , 0x4A , 0x4E , 0x8E , 0x8F , 0x4F , 0x8D , 0x4D , 0x4C , 0x8C ,

0x44 , 0x84 , 0x85 , 0x45 , 0x87 , 0x47 , 0x46 , 0x86 , 0x82 , 0x42 ,

0x43 , 0x83 , 0x41 , 0x81 , 0x80 , 0x40

} ;

unsigned  short  sModbusCrc16 ( INT8U  * chMsg , INT16U  dataLen )

{

unsigned  char  ubCRCHi  =  0xFF ;

unsigned  char  ubCRCLo  =  0xFF ;

unsigned  char  duwIndex ;

while ( dataLen  -- )

{

duwIndex  =  0xff & ( ubCRCHi  ^  * chMsg ++ );

ubCRCHi  =  0xff & ( ubCRCLo  ^  auchCRCHi [ duwIndex ]);

ubCRCLo  =  auchCRCLo [ duwIndex ];

}

return ( ubCRCHi  <<  8  |  ubCRCLo );

}

Оригинален текст

Оценете този превод

Отзивите ви ще се използват за подобряване на Google Преводач

Начало на формуляра

Край на формуляра